## Sheet1
	Header					Payload
	Message start	Sender address	Target address	?	?	?	Payload size	Header CRC	Sender address		Target Address		Function id?			Return # of bytes	Starting address
Byte#	1	2	3	4	5	6	7	8	9	10	11	12	13	14	15	16	17	18	19	20	21	22	23	24	25	26	27	28	29	30	31	32	33	34	35	36	37	38	39	40	41	42	43	44	45	46	47	48	49	50	51	52	53	54	55	56	57	58	59	60	61	62	63	64	65	66	67	68	69	70	71	72	73	74	75	76	77	78	79	80	81	82	83	84	85	86	87	88	89	90	91	92	93	94	95	96	97	98	99	100	101	102	103	104	105	106	107	108	109	110	111	112
Payload byte					1	2	3	4	5	6	7	8	9	10	11	12	13	14	15	16	17	18	19	20	21	22	23	24	25	26	27	28	29	30	31	32	33	34	35	36	37	38	39	40	41	42	43	44	45	46	47	48	49	50	51	52	53	54	55	56	57	58	59	60	61	62	63	64	65	66	67	68	69	70	71	72	73	74	75	76	77	78	79	80	81	82	83	84	85	86	87	88	89	90	91	92	93	94	95	96	97	98	99	100	101	102	103	104
Register value					1	2	3	4	5	6	7	8	9	10	11	12	13	14	15	16	17	18	19	20	21	22	23	24	25	26	27	28	29	30	31	32	33	34	35	36	37	38	39	40	41	42	43	44	45	46	47	48	49	50	51	52	53	54	55	56	57	58	59	60	61	62	63	64	65	66	67	68	69	70	71	72	73	74	75	76	77	78	79	80	81	82	83	84	85	86	87	88	89	90	91	92	93	94
Req#0	69	2	1	84	0	0	0c	f6	2	0	1	0	40	80	0	0a	64	0	d1	b6
Response#1	69	1	2	84	0	0	16	80	1	0	2	0	50	80	0	0a	64	0	21	90	1	62	1	0	61	c6	6	0	7b	71

Req#1	69	2	1	84	0	0	0c	f6	2	0	1	0	40	80	0	32	64	0	bd	b2
Response#1	69	1	2	84	0	0	3e	0d	1	0	2	0	50	80	0	32	64	0	21	90	1	62	1	0	61	c6	6	0	0	0	0	0	0	0	0	12	0a	1	0	9	23	18	0	2f	0	24	0	29	0	2d	0	0	0	0	0	0	0	0	64	8	0	0	67	1	32	88
				T1		T2		T3		T4
Req#2	69	2	1	84	0	0	0c	f6	2	0	1	0	40	80	0	32	96	0	c8	11
Response#2	69	1	2	84	0	0	3e	0d	1	0	2	0	50	80	0	32	96	0	1	0	3c	0	1	0	0f	0	0	0	0	0	0	0	0	1	0	0a	0	5	0	1	0	0	0	e7	ff	23	0	3c	0	0	0	2	0	0	0	1	0	1	0	1	0	0	0	43	af

Req#3	69	2	1	84	0	0	0c	f6	2	0	1	0	40	80	0	32	c8	0	e5	a1
Response#3	69	1	2	84	0	0	3e	0d	1	0	2	0	50	80	0	32	c8	0	1	0	1	0	1	0	0	0	4	0	5	0	55	0	29	0	23	0	32	0	4b	0	1	0	0	0	dc	5	1	0	5a	0	1	0	0	0	0	0	0	0	3c	0	3c	0	1e	0	6	0	c0	ff	b7	67

Req#4
Response#4

Req#3	69	2	1	84	0	0	c	f6	0	0	1	0	40	80	0	1	64	0	ff	cd
Response#3	69	1	2	84	0	0	a	5	1	0	2	0	50	c0	0	6	ff	99

Req#4	69	2	1	84	0	0	e	89	2	0	1	0	8B	80	0	1	82	0	0	0	73	79
Response#4	69	1	2	84	0	0	a	5	1	0	2	0	9b	c0	0	1	22	c5

Req#5	69	2	1	84	0	0	68	31	2	0	1	0	60	80	0	5c	78	0	12	0a	17	1	11	2a	0d	0	2a	0	1a	1	f8	1	0c	fe	0c	fe	11	1	4c	1	b7	ff	b8	ff	f5	1	14	5	14	5	14	5	14	5	c	fe	c	fe	1	0	1	0	1	0	3	0	3	0	1	0	1	0	1	0	1	0	1	0	2	0	2	0	2	0	2	0	3	0	3	0	fb	c3	2	0	25	a8	93	0	0	0	40	0	0	0	0	0	0	0	0	5c	c3
Req#5 (dec)					92	120		120	121	122	123	124	125	126	127	128	129	130	131	132	133	134	135	136	137	138	139	140	141	142	143	144	145	146	147	148	149	150	151	152	153	154	155	156	157	158	159	160	161	162	163	164	165	166	167	168	169	170	171	172	173	174	175	176	177	178	179	180	181	182	183	184	185	186	187	188	189	190	191	192	193	194	195	196	197	198	199	200	201	202	203	204	205	206	207	208	209	210	211
Response#5	69	1	2	84	0	0	0c	84	1	0	2	0	70	80	5c	78	0	2d	f0

Req#6	69	2	1	84	0	0	0c	f6	2	0	1	0	40	80	0	4	fc	0	5b	f5
Response#6	69	1	2	84	0	0	10	1	1	0	2	0	50	80	0	4	fc	0	10	0	0	0	64	8b
				252
Req#7					20
				32

## Sheet2
Packet structure
	Header	Header CRC	PAYLOAD	PAYLOAD CRC
Length (Bytes)	7	1	Date_length from header	2
		CRC-8/DVB-S2		CRC-16/XMODEM

## Registers
Address HEX	DEC	Meaning	Unit	Example HEX	Example DEC	Decoded value	Param1	Param2
64	100				33						no change
65	101				192						no change
66	102				1						no change
67	103				97						no change
68	104				1						no change
69	105				0						no change
6A	106				106						no change
6B	107				166						no change
6C	108				16						no change
6D	109				0						no change
6E	110				0						no change
6F	111				0						no change
70	112				0						no change
71	113				0						no change
72	114				0						no change
73	115				0						no change
74	116				0						no change
75	117				0						no change
76	118				0						no change
77	119				0						no change
78	120	YY – year		12	18	2018-10-01
79	121	MM – month		0a	10	10 – october
7A	122	DD - day		1	1	1 – first
7B	123	??		0	0						0/1
7C	124	HH – hour		9	9	9:35:24
7D	125	MM – minute		23	35
7E	126	SS – second		18	24
7F	127			0	0						no change
80	128	T1_LOW		2f	47	47°C
81	129	T1_HIGH		0	0
82	130	T2_LOW		24	36	36°C	46
83	131	T2_HIGH		0	0		0
84	132	T3_LOW		29	41	41°C	25
85	133	T3_HIGH		0	0		0
86	134	T4_LOW		2d	45	45°C	48	60	30
87	135	T4_HIGH		0	0		0	0	0
88	136	T5?			0		0	0	0		no change
89	137				0		0	0	0		no change
8A	138	T6?			0		0	0	0		no change
8B	139				0		0	0	0		no change
8C	140				0		0	0	0		no change
8D	141				0		0	0	0		no change
8E	142				0		0	0	0		no change
8F	143				0		0	0	0		no change
90	144	Power		64	133	3717 W	0	0	0
91	145	Power – high byte		8	14		0	0	0
92	146			0	0	0	0	0	0
93	147			0	0		0	0	0
94	148	??		1B	141	397	27	27	1B	27-215	Maybe flow or rpms
95	149			0	1		0	0	0	0-1
96	150	Collector pump ON/OFF		0	1	1	0	0	0	0-1
97	151			0	0		0	0	0
98	152	Flow x10	l/min	0	72	72	0	0	0	0-72
99	153			0	0		0	0	0
9A	154	??		0	0	4	0	4	0	5-4-0		drops from 5 to 4 when Power is 0
9B	155			0	0		0	0	0
9C	156	??		0	0	0	0	0	0	1-13	Maybe flow or rpms
9D	157			0	0		0	0	0
9E	158			0	0	0	0	0	0		no change
9F	159			0	0		0	0	0		no change
A0	160			0	0	0	0	0	0		no change
A1	161			0	0		0	0	0		no change
A2	162			0	0	0	0	0	0		no change
A3	163			0	0		0	0	0		no change
A4	164			0	0	0	0	0	0		no change
A5	165			0	0		0	0	0		no change
A6	166	Total energy yield (x10)	kWh	B6	188	32195	195	195	C3	156-165	Changes
A7	167			78	120		120	125	78	125
A8	168			0	0	00	0	0	0	0	no change
A9	169			0	0		0	0	0	0	no change
AA	170	Selected schema		2	2	02	2	2	2	2
AB	171			0	0		0	0	0	0
AC	172	Controller settings – Display – Standby	min	A	10	0A	10	10	A	A
AD	173			0	0		0	0	0	0
AE	174	Controller settings – Display – Brightness		A	10	0A	10	10	A	A
AF	175			0	0		0	0	0	0
B0	176	Controller settings – Sound settings – / Alarm Sound		1	1	01	1	1	1	1
B1	177			0	0		0	0	0	0
B2	178	Controller settings – Sound settings – / Key sound		1	1	01	1	1	1	1
B3	179			0	0		0	0	0	0
B4	180	Language		9	9	09	9	9	9	9
B5	181			0	0		0	0	0	0
B6	182	Fluid freeze Temperature		E7	231	FFE7	231	226	E7	E2	FFE7	65511
B7	183	Fluid freeze Temperature (high byte)		FF	255	-25	255	255	FF	FF
B8	184			19	25	019	25	25	19	19
B9	185			0	0	25	0	0	0	0
BA	186			32	50	032	50	50	32	32
BB	187			0	0	50	0	0	0	0
BC	188			1	1	01	1	1	1	1
BD	189			0	0	1	0	0	0	0
BE	190			64	100	064	100	100	64	64
BF	191			0	0	100	0	0	0	0
C0	192			0	0	00	0	0	0	0
C1	193			0	0	0	0	0	0	0
C2	194			1	1	01	1	1	1	1
C3	195			0	0	1	0	0	0	0
C4	196			6	6	06	6	6	6	6
C5	197			0	0	6	0	0	0	0
C6	198			11	17	011	17	17	11	11
C7	199			0	0	17	0	0	0	0
C8	200			1	1	01	1	1	1	1
C9	201			0	0	1	0	0	0	0
CA	202			6	6	06	6	6	6	6
CB	203			0	0	6	0	0	0	0
CC	204			11	17	011	17	17	11	11
CD	205			0	0	17	0	0	0	0
CE	206	Control parameters – Solar collector type		0	0	00	0	0	0	0
CF	207			0	0	0	0	0	0	0
D0	208	Control parameters - / Temp T1&T2 difference pump on	°C	6	6	06	6	8	6	8
D1	209			0	0	6	0	0	0	0
D2	210			5	5	05	5	5	5	5
D3	211			0	0	5	0	0	0	0
D4	212	Control parameters - / Max Temp T2 OFF collector’s pump		55	85	055	85	84	55	54
D5	213			0	0	85	0	0	0	0
D6	214			29	41	029	41	41	29	29
D7	215			0	0	41	0	0	0	0
D8	216			0	0	00	0	0	0	0
D9	217			0	0	0	0	0	0	0
DA	218			32	50	032	50	50	32	32
DB	219			0	0	50	0	0	0	0
DC	220			4B	75	04B	75	75	4B	4B
DD	221			0	0	75	0	0	0	0
DE	222	Control parameters – / Regulation of collector’s pump		0	0	00	0	1	0	1
DF	223			0	0	0	0	0	0	0
E0	224			30	48	3730	48	0	30	0
E1	225			37	55	14128	55	0	37	0
E2	226			3A	58	53A	58	220	3A	DC
E3	227			5	5	1338	5	5	5	5
E4	228	Control parameters – / Overheat protection of collectors ON		1	1	01	1	1	1	1
E5	229			0	0	1	0	0	0	0
E6	230	Control parameters – / MaxTemp T2 Overheat protection OFF		5A	90	05A	90	89	5A	59
E7	231			0	0	90	0	0	0	0
E8	232	Control parameters – / Freezing protection of collectors ON		0	0	00	0	0	0	0
E9	233			0	0	0	0	0	0	0
EA	234			1	1	01	1	1	1	1
EB	235			0	0	1	0	0	0	0
EC	236			0	0	00	0	0	0	0
ED	237			0	0	0	0	0	0	0
EE	238			0	0	00	0	0	0	0
EF	239			0	0	0	0	0	0	0
F0	240			0	0	00	0	0	0	0
F1	241			0	0	0	0	0	0	0
F2	242			3C	60	03C	60	60	3C	3C
F3	243			0	0	60	0	0	0	0
F4	244			1E	30	01E	30	30	1E	1E
F5	245			0	0	30	0	0	0	0
F6	246			6	6	06	6	6	6	6
F7	247			0	0	6	0	0	0	0
F8	248	Parameters settings – Time program C / Mo-Fr 00-01 thru 15-16		E0	224	FFE0	224	224	E0	E0
F9	249			FF	255	-32	255	255	FF	FF
FA	250			0	0	00			0	0
FB	251			0	0	0			0	0
FC	252			0	0	00			0	0
FD	253			0	0	0			0	0
FE	254			0	0	00			0	0
FF	255			0	0	0			0	0

## Parameters
These are parameters configurable directly on the device – may vary if you have another schema selected

Description SK	Description EN	Sample value	Unit	Memo
Typ schemy	Selected schema	2
RS485-Logicka adresa	RS485 – Logical address	2
RS485-Baudrate	RS485 – baudrate	38400	bps
RS485-Fyzicka adresa	RS485 – physical address	2
Jazyk	Language	Slovensky
Zvuky-Alarm	Sounds – Alarm	Ano
Zvyky-Klavesy	Sounds – Keyboard	Ano
Display-Kontrast	Display – Contrast	10
Display-Display(DIM?)	Display – DIM	10	min
Parametre kolekt. Cerpadla – min		800	rpm
Parametre kolekt. Cerpadla – max		4650	rpm	122A
Prietokomer-Rozmery		Electr.G916
Prietokomer-Nominal		5	l/min
Tepelne medium – T. zamrzania		-25	°C
Parametre cirkulacie - / Time off switching off the circ. Pump		10	min
Parametre cirkulacie - / Time of switching off the circ. Pump		10	min
Parametre cirkulacie - / Min temp T4 switching o the circ.pump		55	°C
Parametre cirkulacie - / Circ. Pump mode		Stála
Parametre cirkulacie - / Switching on the circ.pump		Ano
Cas program?		Od 05:00 do 21:00		Teoreticallly 24 bits on/off for Mo-Fr, Sa, Su (3x24)
Ovladanie parametrov – presostat		nie
Ovladanie parametrov / Úroveň riadenia čerpadla pri štarte		1
Ovladanie parametrov / Čas medzi znížením otáčok kol.čerpadla		10	s
Ovladanie parametrov / Čas medzi zvýšením otáčok kol.čerpadla		150	s
Ovladanie parametrov / Ochrana pred zamŕzaním kolektora		Nie
Ovladanie parametrov / Max T2 pre OFF ochrany prehriatia kolektorov		90	°C
Ovladanie parametrov / Ochrana pred prehriatim kolektorov		Ano
Ovladanie parametrov / Reg. Cerpadla kolektorov		Nie
Ovladanie parametrov / Max T2 pre OFF cerpadla kolektorov		85
Ovladanie parametrov / Rozdiel medzi T1&T2 cerpadlo on		6
Ovladanie parametrov / Solarny kolektor typ		Plochy

## Sheet5
	Parameters settings – Time program C

	0-1	1-2	2-3	3-4	4-5	5-6	6-7	7-8	8-9	9-10	10-11	11-12	12-13	13-14	14-15	15-16	16-17	17-18	18-19	19-20	20-21	21-22	22-23	23-00
Mo-Fr						1	1	1	1	1	1	1	1
Sa						1	1	1	1	1	1	1	1				224	255
Su						1	1	1	1	1	1	1	1

Mo-Fr	1					1	1	1	1	1	1	1	1				225	255
Sa						1	1	1	1	1	1	1	1
Su						1	1	1	1	1	1	1	1
	Register 248					Register 249					Register 250
Mo-Fr	1	1				1	1	1	1	1	1	1	1				227	255
	Register 251					Register 252					Register 253
Sa						1	1	1	1	1	1	1	1
	Register 254					Register 255					Register 256
Su						1	1	1	1	1	1	1	1